SOLAR PV PERFORMANCE ANALYSIS

Plant 1

Dataset Period: 15 May 2020 – 17 June 2020 (34 Days)

Tools Used: Python, Pandas, Scikit-learn, Matplotlib, Seaborn

# 1. Executive Summary

This report presents a comprehensive data analysis of solar PV plant performance using real-world inverter-level generation data and weather sensor readings from Plant 1 in India. The analysis covers a 34-day period across 22 inverters and addresses three core business problems relevant to solar asset management:

- Identifying faulty or underperforming inverters through peer comparison analysis

- Detecting panel cleaning and maintenance requirements using irradiation-to-power efficiency ratios

- Forecasting power generation for the next couple of days to support grid management

Key findings include the identification of two chronically underperforming inverters projecting a combined annual energy loss of approximately 5,256 kWh, detection of one critical maintenance day and five warning days across the 34-day window, and a Random Forest forecasting model achieving an R² of 0.75 with irradiation identified as the dominant generation driver at 69.3% feature importance.

# 2. Dataset Overview

## 2.1 Data Sources

Two datasets were used for this analysis:

| Dataset | Records | Columns | Granularity |
| --- | --- | --- | --- |
| Plant 1 Generation Data | 68,778 | 7 | Per inverter, 15-minute intervals |
| Plant 1 Weather Sensor Data | 3,182 | 6 | Plant level, 15-minute intervals |

## 2.2 Data Structure

The generation dataset captures output at inverter level with 22 unique inverters identified by SOURCE_KEY. Each record contains DC power, AC power, daily yield, and total yield. The sensor dataset provides plant-level weather readings including ambient temperature, module temperature, and solar irradiation from a single optimally placed sensor array.

## 2.3 Data Preparation

- Datetime columns standardised across both files (dayfirst format in generation, ISO format in sensor data)

- Files merged on DATE_TIME using inner join — 3,157 common timestamps retained

- PLANT_ID column dropped (single value: 4135001 throughout)

- Time features engineered: hour, minute, date, day of year, month

- Nighttime rows filtered out using IRRADIATION > 0 threshold

- Final analysis dataset: 38,376 daylight rows x 14 columns, 5am to 7pm solar window

# 3. Finding 1 — Faulty Inverter Detection

## 3.1 Methodology

The core assumption for peer comparison analysis is that all inverters at a plant are exposed to identical weather conditions. Therefore, consistent underperformance relative to peers indicates a structural fault rather than weather-related variation. Each inverter's average DC power during daylight hours was calculated and compared against the plant-wide average. A performance ratio was derived as:

Performance Ratio (%) = (Inverter Avg DC Power / Plant Avg DC Power) x 100

Daily trend analysis was also conducted to distinguish chronic underperformance (structural fault) from isolated bad days (weather or temporary outage).

## 3.2 Results

Two inverters were consistently positioned at the bottom of the performance ranking across all 34 days:

| Inverter ID | Avg DC Power (W) | Performance Ratio | Underperformance | Energy Lost (34 days) | Projected Annual Loss |
| --- | --- | --- | --- | --- | --- |
| bvBOhCH3iADSZry | 5,091.55 W | 89.5% | 10.54% | 262.79 kWh | 2,821 kWh/year |
| 1BY6WEcLGh8j5v7 | 5,173.35 W | 90.9% | 9.10% | 226.81 kWh | 2,435 kWh/year |
| Healthy Avg | 5,691.19 W | 100% | — | — | — |

Combined projected annual energy loss from both underperforming inverters: approximately 5,256 kWh per year.

## 3.3 Key Observations

- Neither inverter crossed the 90% threshold on every single day — making this a soft anomaly rather than a hard failure, which is typical of gradual degradation or partial shading issues

- The underperformance was consistent across all 34 days confirming a structural issue, not random variation

- Daily trend visualisation showed both inverters consistently below the grey band of healthy peers throughout the entire observation period

- Possible root causes include degraded solar panel strings, partial shading, loose wiring connections, or inverter hardware degradation

# 4. Finding 2 — Panel Cleaning & Maintenance Detection

## 4.1 Methodology

A strong correlation of 0.97 was confirmed between irradiation and DC power output, validating irradiation as a reliable baseline for expected generation. Daily efficiency ratio was calculated as:

Efficiency Ratio = Daily Avg DC Power / Daily Avg Irradiation

A 7-day rolling average was used as a dynamic baseline. Days where the efficiency ratio dropped significantly below the rolling average were flagged as potential maintenance or cleaning requirements. Two thresholds were applied:

- Warning threshold: efficiency drop > 2% below 7-day rolling average

- Critical threshold: efficiency drop > 5% below 7-day rolling average

## 4.2 Results

| Date | Efficiency Ratio | Drop vs Rolling Avg | Status |
| --- | --- | --- | --- |
| 2020-05-20 | 13,392.03 | 2.66% | Warning |
| 2020-05-21 | 13,086.75 | 4.21% | Warning |
| 2020-05-22 | 13,194.44 | 3.18% | Warning |
| 2020-05-24 | 13,051.62 | 2.99% | Warning |
| 2020-06-06 | 13,344.54 | 2.26% | Warning |
| 2020-06-07 | 12,808.82 | 5.13% | CRITICAL |

## 4.3 Key Observations

- May 20–22 warning cluster indicates gradual dirt accumulation over that week, suggesting a scheduled cleaning was overdue

- June 6–7 consecutive degradation confirms progressive soiling leading to the critical threshold breach on June 7th

- The pattern of clustered warnings followed by a critical day is a classic panel soiling signature in regions with dry, dusty conditions such as India

- Early warning detection on May 20th could have prevented the June 7th critical event if maintenance had been scheduled promptly

# 5. Finding 3 — Power Generation Forecasting

## 5.1 Methodology

Daily aggregated data across all 22 inverters was used for forecasting total AC power output. Four features were selected based on domain relevance:

- avg_irradiation: solar energy input

- avg_ambient_temp: air temperature affecting panel efficiency

- avg_module_temp: panel surface temperature

- day_number: sequential day counter capturing temporal trend

Two models were trained and compared using a temporal train/test split — the last 5 days were held out as the test set to simulate real-world forecasting. This approach prevents data leakage while simulating the actual use case of predicting near-future generation.

## 5.2 Model Comparison

| Model | MAE (W) | R² Score | Verdict |
| --- | --- | --- | --- |
| Linear Regression | 36,392 | 0.7098 | Good baseline, interpretable |
| Random Forest | 35,373 | 0.7541 | Better performance, recommended |

## 5.3 Feature Importance (Random Forest)

| Feature | Importance | Interpretation |
| --- | --- | --- |
| avg_irradiation | 69.3% | Dominant driver — accurate weather forecast is key |
| avg_module_temp | 18.1% | Panel surface heat affects conversion efficiency |
| day_number | 8.5% | Captures gradual seasonal/temporal trend |
| avg_ambient_temp | 4.1% | Minor influence on overall generation |

## 5.4 Key Observations

- Random Forest outperforms Linear Regression on both MAE and R², making it the recommended model

- Irradiation accounts for 69.3% of predictive power, confirming that solar forecasting is fundamentally a weather forecasting problem

- Both models correctly captured the downward generation trend over the test period but slightly underestimated the sharp drop on June 16–17

- The 34-day training window is a known limitation — with 1–2 years of data, the model would capture seasonal variation and improve significantly

# 6. Limitations & Honest Assessment

The following limitations were identified and should be disclosed transparently:

| Limitation | Impact | Recommendation |
| --- | --- | --- |
| Only 34 days of data | No seasonal patterns captured in forecasting model | Collect 1-2 years of data for robust seasonality modelling |
| Single plant dataset | Model may not generalise to other plants or geographies | Validate on Plant 2 data before production deployment |
| No string/panel level data | Cannot pinpoint exact panel causing inverter underperformance | Integrate string-level monitoring for root cause analysis |
| Weather forecast not used | Forecasting relies on historical weather, not future predictions | Integrate external weather API (e.g. Solcast) for true forecasting |

# 7. Conclusions & Business Impact

This analysis demonstrates that significant operational value can be extracted from existing inverter-level and sensor data without any additional hardware investment. The three key deliverables produced are:

| Finding | Business Value | Action Required |
| --- | --- | --- |
| 2 underperforming inverters identified | ~5,256 kWh/year energy loss recoverable | Immediate inspection of bvBOhCH3iADSZry and 1BY6WEcLGh8j5v7 |
| Panel soiling pattern detected | Early warning prevents critical efficiency loss | Schedule cleaning after 3+ consecutive warning days |
| Forecasting model (R² = 0.75) | Supports grid management decisions | Deploy Random Forest model with irradiation feed |

The methodology developed here is directly scalable to multi-plant monitoring and aligns with industry-standard Performance Ratio analysis used in professional solar asset management.

# 8. Technical Stack

| Tool / Library | Purpose |
| --- | --- |
| Python 3 | Core programming language |
| Pandas | Data manipulation and feature engineering |
| Scikit-learn | Machine learning models (Linear Regression, Random Forest) |
| Matplotlib / Seaborn | Data visualisation and charts |
| NumPy | Numerical computations |
| Kaggle | Dataset source (Solar Power Generation Data — India) |